## Modbus File
EcoStruxure Panel Server
Modbus File
Wireless Concentrator and Modbus Gateway, Datalogger and Energy Server
EcoStruxure offers IoT-enabled architecture and platform.
DOCA0241EN-06
08/2023

## Safety Information
Safety Information
Important Information
Read these instructions carefully, and look at the equipment to become familiar with the device before trying to install, operate, service, or maintain it. The following special messages may appear throughout this documentation or on the equipment to warn of potential hazards or to call attention to information that clarifies or simplifies a procedure.
The addition of this symbol to a “Danger” or “Warning” safety label indicates that an electrical hazard exists which will result in personal injury if the instructions are not followed.
This is the safety alert symbol. It is used to alert you to potential personal injury hazards. Obey all safety messages that follow this symbol to avoid possible injury or death.
Please Note
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
A qualified person is one who has skills and knowledge related to the construction and operation of electrical equipment and its installation, and has received safety training to recognize and avoid the hazards involved.
Cybersecurity Safety Notice
FCC Notice
This device complies with Part 15 of the FCC Rules. Operation is subject to the following two conditions: • This device may not cause harmful interference, and • this device must accept any interference received, including interference that may cause undesired operation. NOTE: This equipment has been tested and found to comply with the limits for a Class A digital device, pursuant to part 15 of the FCC Rules. These limits are designed to provide reasonable protection against harmful interference when the equipment is operating in a commercial environment. This equipment generates, uses, and can radiate radiofrequency energy and, if not installed and used in accordance with the instruction manual, may cause harmful interference to radio communications. Operation of this equipment in a residential area is likely to cause harmful interference in which case the user will be required to correct the interference at his own expense. FCC Caution: Any changes or modifications not expressly approved by the party responsible for compliance could void the user’s authority to operate this equipment. This transmitter must not be co-located or operating in conjunction with any other antenna or transmitter. Radiation Exposure Statement: This equipment complies with FCC radiation exposure limits set forth for an uncontrolled environment. This equipment should be installed and operated with minimum distance 20 cm between the radiator and your body. NOTE: The country code selection is for non-US model only and is not available to all US models. Per FCC regulation, all Wi-Fi product marketed in US must fixed to US operation channels only.

## About the File
About the File
Document Scope
The aim of this file is to provide users, installers, and maintenance personnel with the Modbus registers of: • EcoStruxure™ Panel Server gateways • The wireless devices connected to the Panel Server. These registers provide metering, monitoring, and diagnosis information. For the EcoStruxure Panel Server and each device connected, the list of Modbus registers depends on the application, the type of device and the enabled functions.
Validity Note
This file applies to the following EcoStruxure Panel Server models: • Entry with firmware version 001.007.000 or greater • Universal with firmware version 001.007.000 or greater • Advanced with firmware version 001.007.000 or greater
Convention
EcoStruxure Panel Server is referred to as Panel Server.
Online Information
The information contained in this file is likely to be updated at any time. Schneider Electric strongly recommends that you have the most recent and up-todate version available on https://se.com/ww/en/download
The technical characteristics of the devices described in this file also appear online. To access the information online, go to the Schneider Electric home page at https://www.se.com
Related Documents
| Title of documentation | Reference number
| EcoStruxure Panel Server - User Guide | DOCA0172EN
| EcoStruxure Panel Server Entry - Firmware Release Notes | DOCA0249EN
| EcoStruxure Panel Server Universal - Firmware Release Notes | DOCA0178EN
| EcoStruxure Panel Server Advanced - Firmware Release Notes | DOCA0248EN
You can download these technical publications and other technical information from our website at https://se.com/ww/en/download

## Commercial References
Commercial References of Supported Gateways
Commercial reference | Device name |  | Go to tab
PAS400 | EcoStruxure Panel Server Entry 110–277 Vac/Vdc |  | Panel Server
PAS600 | EcoStruxure Panel Server Universal 110–277 Vac/Vdc |  | Panel Server
PAS600L | EcoStruxure Panel Server Universal 24 Vdc |  | Panel Server
PAS600T | EcoStruxure Panel Server Universal 110–240 Vac/Vdc |  | Panel Server
PAS800 | EcoStruxure Panel Server Advanced 110–277 Vac/Vdc |  | Panel Server
PAS800L | EcoStruxure Panel Server Advanced 24 Vdc |  | Panel Server
Commercial References of Supported Wireless Devices
Commercial reference | Device name | Device family for data models | Go to tab
A9MEM1520 | PowerTag A9 M63 1P+W | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1521 | PowerTag A9 M63 1P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1522 | PowerTag A9 M63 1P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1540 | PowerTag A9 M63 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1541 | PowerTag A9 M63 3P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1542 | PowerTag A9 M63 3P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1543 | PowerTag A9 M63 3P 230V LL | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1560 | PowerTag A9 P63 1P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1561 | PowerTag A9 P63 1P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1562 | PowerTag A9 P63 1P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1563 | PowerTag A9 P63 1P+N Bottom RCBO | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1564 | PowerTag A9 F63 1P+N 110V | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1570 | PowerTag A9 F63 3P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1571 | PowerTag A9 P63 3P+N Top | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1572 | PowerTag A9 P63 3P+N Bottom | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1573 | PowerTag A9 F63 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1574 | PowerTag A9 F63 3P+N 110/230V | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO301P | PowerLogic Tag QO 10-30A 1P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO601P | PowerLogic Tag QO 35-60A 1P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO303P | PowerLogic Tag QO 10-30A 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO603P | PowerLogic Tag QO 35-60A 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO302P | PowerLogic Tag QO 10-30A 2P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTQO602P | PowerLogic Tag QO 35-60A 2P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
LV434020 | PowerTag M250 3P 250A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
LV434022 | PowerTag M630 3P 630A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
LV434021 | PowerTag M250 3P+N 250A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
LV434023 | PowerTag M630 3P+N 630A | PowerTag Energy M250 M630 and PowerLogic Tag E-Frame | PTEnergy250_630-PoTag Efram
PLTE601P | PowerLogic Tag E-Frame 10-60A 1P+N | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTE602P | PowerLogic Tag E-Frame 10-60A 2P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
PLTE603P | PowerLogic Tag E-Frame 10-60A 3P | PowerTag Energy 63 and PowerLogic Tag QO | PTE63-PoTag QO
A9MEM1580 | PowerTag F160 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1590 | PowerTag Rope 200 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1591 | PowerTag Rope 600 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1592 | PowerTag Rope 1000 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
A9MEM1593 | PowerTag Rope 2000 A 3P/3P+N | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR1203P | PowerLogic Tag Rope 120A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR6003P | PowerLogic Tag Rope 600A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR10003P | PowerLogic Tag Rope 1000A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
PLTR20003P | PowerLogic Tag Rope 2000A 3P | PowerTag Energy F160 Rope and PowerLogic Tag Rope | PTE Rope-PoTag Rope
EMS59440 | Easergy TH110 wireless thermal sensor | TH110 | TH110
EMS59443 | Easergy CL110 wireless environmental sensor | CL110 | CL110
SED-CO2-G-5045 | Wireless CO2 sensor | CO2 sensors | CO2 sensors
SED-TRH-G-5045 | Wireless temperature and humidity sensor | Temperature sensors TRH | Temperature sensors TRH
ZBRTT1 | Wireless environmental sensor | Temperature sensors TRH | Temperature sensors TRH
ESST010B0400 | PowerTag A (EwSenseTemp) | Temperature sensors TRH | Temperature sensors TRH
A9XST114 | PowerTag Ambient wireless temperature sensor | Temperature sensors TRH | Temperature sensors TRH
SMT10020 | PowerLogic HeatTag | PowerLogic HeatTag | PowerLogic HeatTag
A9TAA2625 | Acti9 Active ARC iDT40 1PN 25A | Acti9 Active | Acti9 Active
A9TAA1625 | Acti9 ARC iDT40 1PN 25A | Acti9 Active | Acti9 Active
A9TAA2640 | Acti9 Active ARC iDT40 1PN 40A | Acti9 Active | Acti9 Active
A9TAA1640 | Acti9 ARC iDT40 1PN 40A | Acti9 Active | Acti9 Active
A9TAA2225 | Acti9 Active ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAA1225 | Acti9 ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAA2240 | Acti9 Active ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TAA1240 | Acti9 ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TAB2625 | Acti9 Active ARC iC40 1PN 25A | Acti9 Active | Acti9 Active
A9TAB1625 | Acti9 ARC iC40 1PN 25A | Acti9 Active | Acti9 Active
A9TAB2640 | Acti9 Active ARC iC40 1PN 40A | Acti9 Active | Acti9 Active
A9TAB1640 | Acti9 ARC iC40 1PN 40A | Acti9 Active | Acti9 Active
A9TAB2225 | Acti9 Active ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAB1225 | Acti9 ARC iC60 2P 25A | Acti9 Active | Acti9 Active
A9TAB2240 | Acti9 Active ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TAB1240 | Acti9 ARC iC60 2P 40A | Acti9 Active | Acti9 Active
A9TDEC610 | Acti9 Active iCV40N VigiARC 1PN B10 30mA | Acti9 Active | Acti9 Active
A9TDEC613 | Acti9 Active iCV40N VigiARC 1PN B13 30mA | Acti9 Active | Acti9 Active
A9TDEC616 | Acti9 Active iCV40N VigiARC 1PN B16 30mA | Acti9 Active | Acti9 Active
A9TDFC606 | Acti9 Active iCV40N VigiARC 1PN C6 30mA | Acti9 Active | Acti9 Active
A9TDFC610 | Acti9 Active iCV40N VigiARC 1PN C10 30mA | Acti9 Active | Acti9 Active
A9TDFC613 | Acti9 Active iCV40N VigiARC 1PN C13 30mA | Acti9 Active | Acti9 Active
A9TDFC616 | Acti9 Active iCV40N VigiARC 1PN C16 30mA | Acti9 Active | Acti9 Active
A9TDFC625 | Acti9 Active iCV40N VigiARC 1PN C25 30mA | Acti9 Active | Acti9 Active
A9TDFC632 | Acti9 Active iCV40N VigiARC 1PN C32 30mA | Acti9 Active | Acti9 Active
A9TDFC640 | Acti9 Active iCV40N VigiARC 1PN C40 30mA | Acti9 Active | Acti9 Active
A9TDFD606 | Acti9 Active iCV40N VigiARC 1PN C6 30mA | Acti9 Active | Acti9 Active
A9TDFD610 | Acti9 Active iCV40N VigiARC 1PN C10 30mA | Acti9 Active | Acti9 Active
A9TDFD616 | Acti9 Active iCV40N VigiARC 1PN C16 30mA | Acti9 Active | Acti9 Active
A9TDFD620 | Acti9 Active iCV40N VigiARC 1PN C20 30mA | Acti9 Active | Acti9 Active
A9TDFD625 | Acti9 Active iCV40N VigiARC 1PN C25 30mA | Acti9 Active | Acti9 Active
A9TDFD632 | Acti9 Active iCV40N VigiARC 1PN C32 30mA | Acti9 Active | Acti9 Active
A9TPDD610 | Acti9 Active iC40N ARC 1PN B 10A MCB AFD | Acti9 Active | Acti9 Active
A9TPDD613 | Acti9 Active iC40N ARC 1PN B 13A MCB AFD | Acti9 Active | Acti9 Active
A9TPDD616 | Acti9 Active iC40N ARC 1PN B 16A MCB AFD | Acti9 Active | Acti9 Active
A9TPED610 | Acti9 Active iC40N ARC 1PN C 10A MCB AFD | Acti9 Active | Acti9 Active
A9TPED613 | Acti9 Active iC40N ARC 1PN C 13A MCB AFD | Acti9 Active | Acti9 Active
A9TPED616 | Acti9 Active iC40N ARC 1PN C 16A MCB AFD | Acti9 Active | Acti9 Active
A9TPED625 | Acti9 Active iC40N ARC 1PN C 25A MCB AFD | Acti9 Active | Acti9 Active
A9TPED632 | Acti9 Active iC40 ARC 1PN C 32A MCB AFDD | Acti9 Active | Acti9 Active
A9TPED640 | Acti9 Active iC40N ARC 1PN C 40A MCB AFD | Acti9 Active | Acti9 Active
A9TYAE625 | Acti9 VigiARC iDT40 1PN 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYAE640 | ActI9 VigiARC iDT40 1PN 40A 30m A-SI | Acti9 Active | Acti9 Active
A9TYAE225 | Acti9 VigiARC iC60 2P 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYAE240 | Acti9 VigiARC iC60 2P 40A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE625 | Acti9 VigiARC iC40 1PN 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE640 | Acti9 VigiARC iC40 1PN 40A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE225 | Acti9 VigiARC iC60 2P 25A 30m A-SI | Acti9 Active | Acti9 Active
A9TYBE240 | Acti9 VigiARC iC60 2P 40A 30m A-SI | Acti9 Active | Acti9 Active
A9Y6E625 | Acti9 Vigi iDT40 1PN 25 A | Acti9 Active | Acti9 Active
A9Y6E640 | Acti9 Vigi iDT40 1PN 40 A | Acti9 Active | Acti9 Active
A9Y8E625 | Acti9 Vigi iC40 1PN 25 A | Acti9 Active | Acti9 Active
A9Y8E640 | Acti9 Vigi iC40 1PN 40 A | Acti9 Active | Acti9 Active
A9V6E225 | Acti9 Vigi iC60 2P 25 A | Acti9 Active | Acti9 Active
A9V6E240 | Acti9 Vigi iC60 2P 40 A | Acti9 Active | Acti9 Active
A9V8E225 | Acti9 Vigi iC60 2P 25 A | Acti9 Active | Acti9 Active
A9V8E240 | Acti9 Vigi iC60 2P 40 A | Acti9 Active | Acti9 Active
LV429453 | Wireless indication auxiliary for ComPacT NSXm and PowerPacT B-frame | Wireless indication auxiliary | Wireless indication auxiliary
LV429454 | Wireless indication auxiliary for ComPacT NSX, PowerPacT H-, J-, and L-Frame, ComPacT NS, and PowerPacT M-, P-frame | Wireless indication auxiliary | Wireless indication auxiliary
PD100X001 | PowerLogic PD100 Partial discharge monitoring solution | IO module | Partial Discharge Box
A9XMC2D3 | PowerTag C 2DI 230V digital input module | IO module | PowerTagC2DI
A9XMC1D3 | PowerTag C IO 230V digital input output module | IO module | PowerTagCIO

## Modbus Tables
Modbus Table Format and Data Types
EcoStruxure Panel Server System Modbus Registers
The EcoStruxure Panel Server assigns a Modbus address to each of the wireless devices paired with it. The Modbus address of the wireless devices is allocated automatically by the EcoStruxure Panel Server by selecting the first address available from address 100.
The Modbus address of a wireless device can be edited with EcoStruxure Power Commission software with the parameters of the wireless device and updated with a value range from 1 to 247.
To read a value from a particular wireless device, the supervision system uses the Modbus address of the device.
Modbus Register
The address of register number n is n-1. The tables detailed in the tabs of this file provide both register numbers (in decimal format) and corresponding addresses (in hexadecimal format) for the device that belongs to the device family indicated in the tab name of the table. To display the Modbus registers of your device in the correct device family tab, check the Commercial References tab that shows the commercial reference of the devices supported by the EcoStruxure Panel Server and the associated device family. Example: The Commercial References tab shows that PowerTag A9 M63 with commercial reference A9MEM1520 belongs to PowerTag Energy device family. The PowerTag Energy tab shows the Modbus registers available in A9MEM1520. Example of address: address of register number 3000 is 0x0BB7 (2999). NOTE: To know the description of the registers of each associated device (how to use them), print the PDF report of Modbus registers using EcoStruxure Power Commission software (refer to EcoStruxure Power Commission Online Help). This report gives a dynamic knowledge of all the registers potentially to be integrated into the supervision systems including a description of each register.
Table Format
Register tables have the following columns:
| Section | Address | Register | No. | RW | X | Unit | Type | Range | Invalid value | Saved | Function code | Description
| Designation |  | Description
| Section |  | Data category
| Address |  | 16-bit register address in hexadecimal. The address is the data used in the Modbus frame.
| Register |  | 16-bit register number in decimal. Register = Address + 1
| No |  | Number of 16-bit registers that need to be read/written to access the complete information
| R/RW |  | Whether the register is read only (R) or read-write (RW).
| X |  | Scale factor: • A scale of 1 means that the value of the register is the same as the value indicated. • A scale of 10 means that the register contains the value multiplied by 10. The actual value is therefore the value of the register divided by 10. • A scale of 0.1 means that the register contains the value multiplied by 0.1. The actual value is therefore the value of the register multiplied by 10.
| Unit |  | Information unit of measurement: • –: no unit corresponding to the value expressed. • h: hours • D: the unit depends on the connected device.
| Type |  | Coding data type (see Data type table below).
| Range |  | Range of permitted values for the variable, usually a subset of what the format allows. For BITMAP type data, the content of this domain is “–”.
| Invalid value |  | Invalid value for the variable
| Saved |  | Value saved when the power supply to the EcoStruxure Panel Server is switched off: • Y: the value of the register is saved. • N: the value is lost. NOTE: On start-up or reset, the available values are retrieved.
| Function code |  | Code of functions that can be used in the register.
| Description |  | Information about the register and the restrictions that apply.
Access to Modbus Registers from the Commercial Reference
Each supported wireless device is referenced in the Commercial References tab with: • Its commercial reference • Its device name • Its device family In the Commercial References tab, click the commercial reference of a device to automatically access the tab detailing its Modbus registers.
Filtering Data of Modbus Registers
In the tab of a device family, you can filter data of the registers using the filter function.
Data Types
| UINT16 |  | 16-bit unsigned integer (1 word) |  |  |  | 0 to 65535
| INT32 |  | 32-bit signed integer (2 words) |  |  |  | -2 147 483 648 to +2 147 483 647
| UINT32 |  | 32-bit unsigned integer (2 words) |  |  |  | 0 to 4 294 967 295
| INT64 |  | 64-bit signed integer (4 words) |  |  |  | -9 223 372 036 854 775 808 to 9 223 372 036 854 775 807
| UINT64 |  | 64-bit unsigned integer (4 words) |  |  |  | 0 to 18 446 744 073 709 600 000
| Float32 |  | 32-bit value (2 words) |  |  |  | -3.4028E+38 to +3.4028E+38
| ASCII |  | 8-bit alphanumeric character |  |  |  | Table of ASCII characters
| BITMAP |  | 16-bit field (1 word) |  |  |  | –
| DATETIME |  | Date and time in IEC 60870-5 format |  |  |  | See DATETIME below
Big-Endian Format
INT32, UINT32, INT64, and UINT64 variables are stored in big-endian format: the most significant register is transmitted first and the least significant register is transmitted at last place.
INT32, UINT32, INT64, and UINT64 variables are made of UINT16 variables.
The formulas to calculate the decimal value of these variables are: • INT32: (0-bit31)x231 + bit30x230 + bit29x229 + ...bit1x21 + bit0x20 • UINT32: bit31x231 + bit30x230 + bit29x229 + ...bit1x21 + bit0x20 • INT64: (0-bit63)x263 + bit62x262 + bit61x261 + ...bit1x21 + bit0x20 • UINT64: bit63x263 + bit62x262 + bit61x261 + ...bit1x21 + bit0x20
Example:
The total active energy delivered by a PowerTag Energy M250 M630 is an INT64 variable coded in registers 3208 to 3211.
If the values in the registers are: • register 3208 = 0 • register 3209 = 0 • register 3210 = 0x0017 or 23 • register 3211 = 0x9692 or 38546 as UINT16 variable and -26990 as INT16 variable (use the UINT16 value to calculate the value of the total active energy).
Then the total active energy is equal to 0x248 + 0x232 + 23x216 + 38546x20 = 1545874 Wh.
Data Type: Float32
Data type Float32 is represented in the single precision IEEE 754 (IEEE standard for floating-point arithmetic). A value N is calculated as indicated below:
N = (-1)S x 2E-127 x (1+M)
| Coefficient |  | Stands for |  | Description |  |  |  |  | Number of Bits
| S |  | Sign |  | Defines the sign of the value: 0 = positive 1 = negative |  |  |  |  | 1 bit
| E |  | Exponent |  | Excess 127 binary integer added. When 0 < E < 255, the actual exponent is: e = E - 127. |  |  |  |  | 8 bits
| M |  | Mantissa |  | Magnitude, normalized binary significant |  |  |  |  | 23 bits
Example:
0 = 0 00000000 00000000000000000000000 -1.5 = 1 01111111 10000000000000000000000 with: • S = 1 • E = 01111111 = 127 • M = 10000000000000000000000 = 1x2-1 + 0x2-2 +...+ 0x2-23 = 0.5 • N = (-1) x 20 x (1+0.5) = -1.5
Data Type: DATETIME
DATETIME is a data type used to code date and time defined by IEC 60870-5 standard.
| Register | Type | Bit | Range |  | Description
| 1 | UINT16 | 0–6 | 0x00–0x7F |  | Year:
0x00 (00) to 0x7F (127) correspond to years 2000 to 2127.
For example, 0x0D (13) corresponds to year 2013.
|  |  | 7–15 | – |  | Reserved
| 2 | UINT16 | 0–4 | 0x01–0x1F |  | Day
|  |  | 5–7 | – |  | Reserved
|  |  | 8–11 | 0x00–0x0C |  | Month
|  |  | 12–15 | – |  | Reserved
| 3 | UINT16 | 0–5 | 0x00–0x3B |  | Minutes
|  |  | 6–7 | – |  | Reserved
|  |  | 8–12 | 0x00–0x17 |  | Hours
|  |  | 13–15 | – |  | Reserved
| 4 | UINT16 | 0–15 | 0x0000–0xEA5F |  | Milliseconds
Example of Modbus Frames
Request
| Definition |  | Number of Bytes |  | Value | Comment
| Server number |  | 1 byte |  | 0x05 | EcoStruxure Panel Server Modbus Address
| Function code |  | 1 byte |  | 0x03 | Reads n output or internal words
| Address |  | 2 bytes |  | 0x36E2 | Address of a consumption meter whose address is 14050 in decimal notation.
| Number of words |  | 2 bytes |  | 0x002C | Reads 44 16-bit registers.
| CRC |  | 2 bytes |  | xxxx | Value of CRC16
Response
| Definition |  | Number of Bytes |  | Value | Comment
| Server number |  | 1 byte |  | 0x05 | EcoStruxure Panel Server Modbus Address
| Function code |  | 1 byte |  | 0x03 | Reads n output or internal words
| Number of Bytes |  | 2 bytes |  | 0x0058 | Number of bytes read
| Number of words read |  | 88 bytes |  | – | Reads 44 16-bit registers.
| CRC |  | 2 bytes |  | xxxx | Value of CRC16

## Panel Server
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x000A | 11 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product range
Identification | 0x001A | 27 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product family
Identification | 0x002A | 43 | 17 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Vendor URL
Identification | 0x003C | 61 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial Reference - Example "PAS600L"
Identification | 0x0050 | 81 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server hardware version on 11 ASCII characters, valid for firmware version 001.008.007 and later. Example: 000.000.001
Identification | 0x0064 | 101 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Serial number on 12 ASCII characters; 11 alphanumeric digits maximum [SN] or [S/N]: PP YY WW [D[nnnn]] • PP: Plant • YY: Year in decimal notation [05...99] • WW: Week in decimal notation [1...53] • D: Day of the week in decimal notation [1...7] • nnnn: Sequence of numbers [0001...10.000–1]
Date and Time | 0x0073 | 116 | 4 | RW | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | N | 3, 100-4, 16 | Indicates the year, month, day, hour, minute and millisecond on EcoStruxure Panel Server. Refer to DATETIME.
Identification | 0x0078 | 121 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | EcoStruxure Panel Server firmware version on 11 ASCII characters, valid for firmware version 001.008.007 and later. Example: 001.008.007
Identification | 0x007E | 127 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Product capability
Identification | 0x008E | 143 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Additionnal product capability
Health State | 0x009E | 159 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Health state of EcoStruxure Panel Server • 0 = Nominal • 1 = Degraded • 2 = Out of order
Identification | 0x009F | 160 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Manufacturer Name - "Schneider Electric"
List of wireless devices | 0x01F4 | 501 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 1
List of wireless devices | 0x01F8 | 505 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 1
List of wireless devices | 0x01F9 | 506 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 2
List of wireless devices | 0x01FD | 510 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 2
List of wireless devices | 0x01FE | 511 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 3
List of wireless devices | 0x0202 | 515 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 3
List of wireless devices | 0x0203 | 516 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 4
List of wireless devices | 0x0207 | 520 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 4
List of wireless devices | 0x0208 | 521 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 5
List of wireless devices | 0x020C | 525 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 5
List of wireless devices | 0x020D | 526 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 6
List of wireless devices | 0x0211 | 530 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 6
List of wireless devices | 0x0212 | 531 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 7
List of wireless devices | 0x0216 | 535 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 7
List of wireless devices | 0x0217 | 536 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 8
List of wireless devices | 0x021B | 540 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 8
List of wireless devices | 0x021C | 541 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 9
List of wireless devices | 0x0220 | 545 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 9
List of wireless devices | 0x0221 | 546 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 10
List of wireless devices | 0x0225 | 550 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 10
List of wireless devices | 0x0226 | 551 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 11
List of wireless devices | 0x022A | 555 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 11
List of wireless devices | 0x022B | 556 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 12
List of wireless devices | 0x022F | 560 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 12
List of wireless devices | 0x0230 | 561 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 13
List of wireless devices | 0x0234 | 565 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 13
List of wireless devices | 0x0235 | 566 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 14
List of wireless devices | 0x0239 | 570 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 14
List of wireless devices | 0x023A | 571 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 15
List of wireless devices | 0x023E | 575 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 15
List of wireless devices | 0x023F | 576 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 16
List of wireless devices | 0x0243 | 580 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 16
List of wireless devices | 0x0244 | 581 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 17
List of wireless devices | 0x0248 | 585 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 17
List of wireless devices | 0x0249 | 586 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 18
List of wireless devices | 0x024D | 590 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 18
List of wireless devices | 0x024E | 591 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 19
List of wireless devices | 0x0252 | 595 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 19
List of wireless devices | 0x0253 | 596 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 20
List of wireless devices | 0x0257 | 600 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 20
List of wireless devices | 0x0258 | 601 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 21
List of wireless devices | 0x025C | 605 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 21
List of wireless devices | 0x025D | 606 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 22
List of wireless devices | 0x0261 | 610 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 22
List of wireless devices | 0x0262 | 611 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 23
List of wireless devices | 0x0266 | 615 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 23
List of wireless devices | 0x0267 | 616 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 24
List of wireless devices | 0x026B | 620 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 24
List of wireless devices | 0x026C | 621 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 25
List of wireless devices | 0x0270 | 625 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 25
List of wireless devices | 0x0271 | 626 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 26
List of wireless devices | 0x0275 | 630 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 26
List of wireless devices | 0x0276 | 631 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 27
List of wireless devices | 0x027A | 635 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 27
List of wireless devices | 0x027B | 636 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 28
List of wireless devices | 0x027F | 640 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 28
List of wireless devices | 0x0280 | 641 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 29
List of wireless devices | 0x0284 | 645 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 29
List of wireless devices | 0x0285 | 646 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 30
List of wireless devices | 0x0289 | 650 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 30
List of wireless devices | 0x028A | 651 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 31
List of wireless devices | 0x028E | 655 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 31
List of wireless devices | 0x028F | 656 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 32
List of wireless devices | 0x0293 | 660 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 32
List of wireless devices | 0x0294 | 661 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 33
List of wireless devices | 0x0298 | 665 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 33
List of wireless devices | 0x0299 | 666 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 34
List of wireless devices | 0x029D | 670 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 34
List of wireless devices | 0x029E | 671 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 35
List of wireless devices | 0x02A2 | 675 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 35
List of wireless devices | 0x02A3 | 676 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 36
List of wireless devices | 0x02A7 | 680 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 36
List of wireless devices | 0x02A8 | 681 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 37
List of wireless devices | 0x02AC | 685 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 37
List of wireless devices | 0x02AD | 686 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 38
List of wireless devices | 0x02B1 | 690 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 38
List of wireless devices | 0x02B2 | 691 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 39
List of wireless devices | 0x02B6 | 695 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 39
List of wireless devices | 0x02B7 | 696 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 40
List of wireless devices | 0x02BB | 700 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 40
List of wireless devices | 0x02BC | 701 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 41
List of wireless devices | 0x02C0 | 705 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 41
List of wireless devices | 0x02C1 | 706 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 42
List of wireless devices | 0x02C5 | 710 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 42
List of wireless devices | 0x02C6 | 711 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 43
List of wireless devices | 0x02CA | 715 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 43
List of wireless devices | 0x02CB | 716 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 44
List of wireless devices | 0x02CF | 720 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 44
List of wireless devices | 0x02D0 | 721 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 45
List of wireless devices | 0x02D4 | 725 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 45
List of wireless devices | 0x02D5 | 726 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 46
List of wireless devices | 0x02D9 | 730 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 46
List of wireless devices | 0x02DA | 731 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 47
List of wireless devices | 0x02DE | 735 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 47
List of wireless devices | 0x02DF | 736 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 48
List of wireless devices | 0x02E3 | 740 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 48
List of wireless devices | 0x02E4 | 741 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 49
List of wireless devices | 0x02E8 | 745 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 49
List of wireless devices | 0x02E9 | 746 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 50
List of wireless devices | 0x02ED | 750 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 50
List of wireless devices | 0x02EE | 751 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 51
List of wireless devices | 0x02F2 | 755 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 51
List of wireless devices | 0x02F3 | 756 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 52
List of wireless devices | 0x02F7 | 760 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 52
List of wireless devices | 0x02F8 | 761 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 53
List of wireless devices | 0x02FC | 765 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 53
List of wireless devices | 0x02FD | 766 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 54
List of wireless devices | 0x0301 | 770 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 54
List of wireless devices | 0x0302 | 771 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 55
List of wireless devices | 0x0306 | 775 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 55
List of wireless devices | 0x0307 | 776 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 56
List of wireless devices | 0x030B | 780 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 56
List of wireless devices | 0x030C | 781 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 57
List of wireless devices | 0x0310 | 785 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 57
List of wireless devices | 0x0311 | 786 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 58
List of wireless devices | 0x0315 | 790 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 58
List of wireless devices | 0x0316 | 791 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 59
List of wireless devices | 0x031A | 795 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 59
List of wireless devices | 0x031B | 796 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 60
List of wireless devices | 0x031F | 800 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 60
List of wireless devices | 0x0320 | 801 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 61
List of wireless devices | 0x0324 | 805 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 61
List of wireless devices | 0x0325 | 806 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 62
List of wireless devices | 0x0329 | 810 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 62
List of wireless devices | 0x032A | 811 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 63
List of wireless devices | 0x032E | 815 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 63
List of wireless devices | 0x032F | 816 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 64
List of wireless devices | 0x0333 | 820 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 64
List of wireless devices | 0x0334 | 821 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 65
List of wireless devices | 0x0338 | 825 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 65
List of wireless devices | 0x0339 | 826 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 66
List of wireless devices | 0x033D | 830 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 66
List of wireless devices | 0x033E | 831 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 67
List of wireless devices | 0x0342 | 835 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 67
List of wireless devices | 0x0343 | 836 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 68
List of wireless devices | 0x0347 | 840 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 68
List of wireless devices | 0x0348 | 841 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 69
List of wireless devices | 0x034C | 845 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 69
List of wireless devices | 0x034D | 846 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 70
List of wireless devices | 0x0351 | 850 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 70
List of wireless devices | 0x0352 | 851 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 71
List of wireless devices | 0x0356 | 855 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 71
List of wireless devices | 0x0357 | 856 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 72
List of wireless devices | 0x035B | 860 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 72
List of wireless devices | 0x035C | 861 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 73
List of wireless devices | 0x0360 | 865 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 73
List of wireless devices | 0x0361 | 866 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 74
List of wireless devices | 0x0365 | 870 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 74
List of wireless devices | 0x0366 | 871 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 75
List of wireless devices | 0x036A | 875 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 75
List of wireless devices | 0x036B | 876 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 76
List of wireless devices | 0x036F | 880 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 76
List of wireless devices | 0x0370 | 881 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 77
List of wireless devices | 0x0374 | 885 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 77
List of wireless devices | 0x0375 | 886 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 78
List of wireless devices | 0x0379 | 890 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 78
List of wireless devices | 0x037A | 891 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 79
List of wireless devices | 0x037E | 895 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 79
List of wireless devices | 0x037F | 896 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 80
List of wireless devices | 0x0383 | 900 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 80
List of wireless devices | 0x0384 | 901 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 81
List of wireless devices | 0x0388 | 905 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 81
List of wireless devices | 0x0389 | 906 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 82
List of wireless devices | 0x038D | 910 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 82
List of wireless devices | 0x038E | 911 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 83
List of wireless devices | 0x0392 | 915 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 83
List of wireless devices | 0x0393 | 916 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 84
List of wireless devices | 0x0397 | 920 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 84
List of wireless devices | 0x0398 | 921 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 85
List of wireless devices | 0x039C | 925 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 85
List of wireless devices | 0x039D | 926 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 86
List of wireless devices | 0x03A1 | 930 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 86
List of wireless devices | 0x03A2 | 931 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 87
List of wireless devices | 0x03A6 | 935 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 87
List of wireless devices | 0x03A7 | 936 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 88
List of wireless devices | 0x03AB | 940 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 88
List of wireless devices | 0x03AC | 941 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 89
List of wireless devices | 0x03B0 | 945 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 89
List of wireless devices | 0x03B1 | 946 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 90
List of wireless devices | 0x03B5 | 950 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 90
List of wireless devices | 0x03B6 | 951 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 91
List of wireless devices | 0x03BA | 955 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 91
List of wireless devices | 0x03BB | 956 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 92
List of wireless devices | 0x03BF | 960 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 92
List of wireless devices | 0x03C0 | 961 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 93
List of wireless devices | 0x03C4 | 965 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 93
List of wireless devices | 0x03C5 | 966 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 94
List of wireless devices | 0x03C9 | 970 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 94
List of wireless devices | 0x03CA | 971 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 95
List of wireless devices | 0x03CE | 975 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 95
List of wireless devices | 0x03CF | 976 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 96
List of wireless devices | 0x03D3 | 980 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 96
List of wireless devices | 0x03D4 | 981 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 97
List of wireless devices | 0x03D8 | 985 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 97
List of wireless devices | 0x03D9 | 986 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 98
List of wireless devices | 0x03DD | 990 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 98
List of wireless devices | 0x03DE | 991 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 99
List of wireless devices | 0x03E2 | 995 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 99
List of wireless devices | 0x03E3 | 996 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | RFID of wireless device 100
List of wireless devices | 0x03E7 | 1000 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual address of wireless device 100
Local Digital Inputs | 0x03E8 | 1001 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI1 validity. If a device is connected on DI1, a valid value is returned (= 1). Otherwise an invalid value is returned.
Local Digital Inputs | 0x03E9 | 1002 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI2 validity. If a device is connected on DI2, a valid value is returned (= 1). Otherwise an invalid value is returned.
Local Digital Inputs | 0x03EA | 1003 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI1 input mode • 0 = Pulse • 1 = Status
Local Digital Inputs | 0x03EB | 1004 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | DI2 input mode • 0 = Pulse • 1 = Status
Local Digital Inputs | 0x03EC | 1005 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | User application name of the device connected on DI1
Local Digital Inputs | 0x0400 | 1025 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | User application name of the device connected on DI2
Local Digital Inputs | 0x0414 | 1045 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Electrical label of the device connected on DI1
Local Digital Inputs | 0x0417 | 1048 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Electrical label of the device connected on DI2
Local Digital Inputs | 0x041A | 1051 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Usage of the device connected to DI1: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Local Digital Inputs | 0x041B | 1052 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Usage of the device connected to DI2: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Local Digital Inputs | 0x041C | 1053 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Logical status of the Digital Input DI1 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Local Digital Inputs | 0x041D | 1054 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Logical status of the Digital Input DI2 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Local Digital Inputs | 0x041E | 1055 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI1 operating time
Local Digital Inputs | 0x0420 | 1057 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI2 operating time
Local Digital Inputs | 0x0422 | 1059 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI1 operating time
Local Digital Inputs | 0x0424 | 1061 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI2 operating time
Local Digital Inputs | 0x0426 | 1063 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI1 last reset operating time date
Local Digital Inputs | 0x042A | 1067 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI2 last reset operating time date
Local Digital Inputs | 0x042E | 1071 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI1 operation counter
Local Digital Inputs | 0x0430 | 1073 | 2 | R | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4 | Non resettable DI2 operation counter
Local Digital Inputs | 0x0432 | 1075 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI1 operation counter
Local Digital Inputs | 0x0434 | 1077 | 2 | RW | - | - | UINT32 |  | 0xFFFFFFFF | Y | 3, 100-4, 16 | Resettable DI2 operation counter
Local Digital Inputs | 0x0436 | 1079 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI1 last reset operation counter date
Local Digital Inputs | 0x043A | 1083 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | DI2 last reset operation counter date
Local Digital Inputs | 0x043E | 1087 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Pulse weight of device connected on DI1 if DI1 mode is set to Pulse
Local Digital Inputs | 0x0440 | 1089 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Pulse weight of device connected on DI2 if DI2 mode is set to Pulse
Local Digital Inputs | 0x0442 | 1091 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Offset applied on DI1 is DI1 mode if set to Pulse
Local Digital Inputs | 0x0446 | 1095 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Offset applied on DI2 is DI2 mode if set to Pulse
Local Digital Inputs | 0x044A | 1099 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Non-resettable pulse counter on DI1 if DI1 mode is set to Pulse
Local Digital Inputs | 0x044E | 1103 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Non-resettable pulse counter on DI2 if DI2 mode is set to Pulse
Local Digital Inputs | 0x0452 | 1107 | 4 | RW | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Resettable DI1 pulse count
Local Digital Inputs | 0x0456 | 1111 | 4 | RW | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Resettable DI2 pulse count
Local Digital Inputs | 0x045A | 1115 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Date of last reset pulse counter for DI1
Local Digital Inputs | 0x045E | 1119 | 4 | R | - | - | DATE-TIME |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Date of last reset pulse counter for DI2
Local Digital Inputs | 0x0462 | 1123 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Metering accumulated value on DI1 if DI1 mode is set to Pulse
Local Digital Inputs | 0x0466 | 1127 | 4 | R | - | - | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Metering accumulated value on DI2 if DI2 mode is set to Pulse
Local Digital Inputs | 0x0494 | 1173 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Measured flow unit on DI1 if DI1 mode is set to Pulse
Local Digital Inputs | 0x0496 | 1175 | 2 | R | - | - | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Measured flow unit on DI2 if DI2 mode is set to Pulse
Local Digital Inputs | 0x04C2 | 1219 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Commodity of device connected to DI1 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Local Digital Inputs | 0x04C3 | 1220 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Commodity of device connected to DI2 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Local Digital Inputs | 0x04C4 | 1221 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Local Digital Inputs | 0x04C5 | 1222 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Local Digital Inputs | 0x04C6 | 1223 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Digital input DI1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Local Digital Inputs | 0x04C7 | 1224 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Digital input DI2 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Local Digital Inputs | 0x04C8 | 1225 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input DI1 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Local Digital Inputs | 0x04C9 | 1226 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input DI2 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Local Digital Inputs | 0x04CA | 1227 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input DI1 when DI1 is defined as 'Custom'
Local Digital Inputs | 0x04D4 | 1237 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input DI2 when DI2 is defined as 'Custom'
Local Digital Inputs | 0x04DE | 1247 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input DI1 when DI1 is defined as 'Custom'
Local Digital Inputs | 0x04E8 | 1257 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input DI2 when DI2 is defined as 'Custom'
Local Digital Inputs | 0x04F2 | 1267 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input DI1 when DI1 is defined as 'Custom'
Local Digital Inputs | 0x04FC | 1277 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input DI2 when DI2 is defined as 'Custom'
Local Digital Inputs | 0x0506 | 1287 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Feature assigned to digital input 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0507 | 1288 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Feature assigned to digital input 0 None (None/empty) None/empty (None/empty) 1 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 2 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 3 ElectricalMeasurement.DeliveredActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 4 ElectricalMeasurement.ReceivedActiveEnergyPhsA (Wh) ElectricalMeasurement.RmsActivePowerPhsA (W) 5 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 6 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 7 ElectricalMeasurement.DeliveredActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 8 ElectricalMeasurement.ReceivedActiveEnergyPhsB (Wh) ElectricalMeasurement.RmsActivePowerPhsB (W) 9 ElectricalMeasurement.Delivered+ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 10 ElectricalMeasurement.Delivered-ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 11 ElectricalMeasurement.DeliveredActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 12 ElectricalMeasurement.ReceivedActiveEnergyPhsC (Wh) ElectricalMeasurement.RmsActivePowerPhsC (W) 13 ElectricalMeasurement.TotalDelivered+ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 14 ElectricalMeasurement.TotalDelivered-ReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 15 ElectricalMeasurement.TotalDeliveredActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 16 ElectricalMeasurement.TotalReceivedActiveEnergy (Wh) ElectricalMeasurement.TotalRmsActivePower (W) 17 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 18 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 19 ElectricalMeasurement.DeliveredReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 20 ElectricalMeasurement.ReceivedReactiveEnergyPhsA (Varh) ElectricalMeasurement.RmsReactivePowerPhsA (Var) 21 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 22 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 23 ElectricalMeasurement.DeliveredReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 24 ElectricalMeasurement.ReceivedReactiveEnergyPhsB (Varh) ElectricalMeasurement.RmsReactivePowerPhsB (Var) 25 ElectricalMeasurement.Delivered+ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 26 ElectricalMeasurement.Delivered-ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 27 ElectricalMeasurement.DeliveredReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 28 ElectricalMeasurement.ReceivedReactiveEnergyPhsC (Varh) ElectricalMeasurement.RmsReactivePowerPhsC (Var) 29 ElectricalMeasurement.TotalDelivered+ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 30 ElectricalMeasurement.TotalDelivered-ReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 31 ElectricalMeasurement.TotalDeliveredReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 32 ElectricalMeasurement.TotalReceivedReactiveEnergy (Varh) ElectricalMeasurement.TotalRmsReactivePower (Var) 33 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 34 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 35 ElectricalMeasurement.DeliveredApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 36 ElectricalMeasurement.ReceivedApparentEnergyPhsA (VAh) ElectricalMeasurement.RmsApparentPowerPhsA (VA) 37 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 38 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 39 ElectricalMeasurement.DeliveredApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 40 ElectricalMeasurement.ReceivedApparentEnergyPhsB (VAh) ElectricalMeasurement.RmsApparentPowerPhsB (VA) 41 ElectricalMeasurement.Delivered+ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 42 ElectricalMeasurement.Delivered-ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 43 ElectricalMeasurement.DeliveredApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 44 ElectricalMeasurement.ReceivedApparentEnergyPhsC (VAh) ElectricalMeasurement.RmsApparentPowerPhsC (VA) 45 ElectricalMeasurement.TotalDelivered+ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 46 ElectricalMeasurement.TotalDelivered-ReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 47 ElectricalMeasurement.TotalDeliveredApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 48 ElectricalMeasurement.TotalReceivedApparentEnergy (VAh) ElectricalMeasurement.TotalRmsApparentPower (VA) 49 WaterVolume (m³) WaterFlowRate ( m³/h) 50 GasVolume (m³) GasFlowRate ( m³/h) 51 HeatEnergy (Wh) HeatPower (W) 52 ChilledEnergy (Wh) ChilledPower (W) 53 Custom Custom
Local Digital Inputs | 0x0508 | 1289 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Metering accumulated name for DI1. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x051C | 1309 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Metering accumulated name for DI2 Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0530 | 1329 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Metering accumulated custom unit for DI1. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0544 | 1349 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Metering accumulated custom unit for DI2. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0558 | 1369 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Flow name for DI1. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x056C | 1389 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Custom Flow name for DI2. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0580 | 1409 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Measured Flow custom unit for DI1. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Local Digital Inputs | 0x0594 | 1429 | 20 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Measured Flow custom unit for DI2. Unit defined at Commissioning time. Used only if unit is custom. Only applicable if DI mode is "Pulse"
Identification | 0x1605 | 5638 | 32 | R | - | - | ASCII |  | 0x00000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server user application name
Identification | 0xF002 | 61443 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | EcoStruxure Panel Server product identifier
Identification | 0xF003 | 61444 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | EcoStruxure Panel Server product model

## PTE63-PoTag QO
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CED | 3310 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Active power threshold for load operating time counter. Counter starts above the threshold value.
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1394 | 5013 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x139C | 5021 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy received count negatively (not resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13BC | 5053 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13C4 | 5061 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (not resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E4 | 5093 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x13EC | 5101 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (not resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x140C | 5133 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1414 | 5141 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (not resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7927 | 31016 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Mounting position • 0 = Not configured • 1 = Top • 2 = Bottom • 3 = Not applicable
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PTEnergy250_630-PoTag Efram
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Frequency Metering Data | 0x0C25 | 3110 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC frequency
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0C87 | 3208 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered count positively (not resettable)
Energy Data - Legacy Zone | 0x0C8B | 3212 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy received (not resettable)
Energy Data - Legacy Zone | 0x0C8F | 3216 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered – received (not resettable)
Energy Data - Legacy Zone | 0x0C93 | 3220 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered – received (not resettable)
Energy Data - Legacy Zone | 0x0C97 | 3224 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered – received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CED | 3310 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Active power threshold for load operating time counter. Counter starts above the threshold value.
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7927 | 31016 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Mounting position • 0 = Not configured • 1 = Top • 2 = Bottom • 3 = Not applicable
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792A | 31019 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Electrical network system type • 0 = Unknown system type • 3 = 3PH3W • 11= 3PH4W
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PTE Rope-PoTag Rope
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Current Metering Data | 0x0BBD | 3006 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on Neutral
Voltage Metering Data | 0x0BCB | 3020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage A-B
Voltage Metering Data | 0x0BCD | 3022 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage B-C
Voltage Metering Data | 0x0BCF | 3024 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-phase voltage C-A
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BF5 | 3062 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase A
Power Metering Data | 0x0BF7 | 3064 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase B
Power Metering Data | 0x0BF9 | 3066 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Reactive power on phase C
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0BFD | 3070 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase A
Power Metering Data | 0x0BFF | 3072 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase B
Power Metering Data | 0x0C01 | 3074 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Apparent power on phase C
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C05 | 3078 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase A
Power Factor Metering Data | 0x0C07 | 3080 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase B
Power Factor Metering Data | 0x0C09 | 3082 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Power factor on phase C
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Power Factor Metering Data | 0x0C0D | 3086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power factor sign convention • 0 = IEC • 1 = IEEE
Frequency Metering Data | 0x0C25 | 3110 | 2 | R | - | Hz | Float32 |  | 0xFFC00000 | N | 3, 100-4 | AC frequency
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0C87 | 3208 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered count positively (not resettable)
Energy Data - Legacy Zone | 0x0C8B | 3212 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CED | 3310 | 2 | R | - | W | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Active power threshold for load operating time counter. Counter starts above the threshold value.
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1394 | 5013 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x139C | 5021 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy received count negatively (not resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13BC | 5053 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13C4 | 5061 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (not resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E4 | 5093 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x13EC | 5101 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (not resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x140C | 5133 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1414 | 5141 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (not resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x143C | 5181 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Energy Data – New Zone | 0x144C | 5197 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy received count negatively (not resettable)
Energy Data – New Zone | 0x1470 | 5233 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A delivered (resettable)
Energy Data – New Zone | 0x1474 | 5237 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x1478 | 5241 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A received (resettable)
Energy Data – New Zone | 0x147C | 5245 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A received (not resettable)
Energy Data – New Zone | 0x1498 | 5273 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B delivered (resettable)
Energy Data – New Zone | 0x149C | 5277 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x14A0 | 5281 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B received (resettable)
Energy Data – New Zone | 0x14A4 | 5285 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B received (not resettable)
Energy Data – New Zone | 0x14C0 | 5313 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C delivered (resettable)
Energy Data – New Zone | 0x14C4 | 5317 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x14C8 | 5321 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C received (resettable)
Energy Data – New Zone | 0x14CC | 5325 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C received (not resettable)
Energy Data – New Zone | 0x14F4 | 5365 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy delivered + received (resettable)
Energy Data – New Zone | 0x14F8 | 5369 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy delivered + received (not resettable)
Energy Data – New Zone | 0x150C | 5389 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase A (resettable)
Energy Data – New Zone | 0x1510 | 5393 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase A (not resettable)
Energy Data – New Zone | 0x1534 | 5429 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase B (resettable)
Energy Data – New Zone | 0x1538 | 5433 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase B (not resettable)
Energy Data – New Zone | 0x155C | 5469 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase C (resettable)
Energy Data – New Zone | 0x1560 | 5473 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase C (not resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7927 | 31016 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Mounting position • 0 = Not configured • 1 = Top • 2 = Bottom • 3 = Not applicable
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792A | 31019 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Electrical network system type • 0 = Unknown system type • 3 = 3PH3W • 11= 3PH4W
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## TH110
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## CL110
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Diagnostic Data | 0x0CF3 | 3316 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Battery voltage
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## CO2 sensors
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Diagnostic Data | 0x0CF3 | 3316 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Battery voltage
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Ambient Data | 0x0FAE | 4015 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | CO2 (Example:5000 ppm represented as 0,005)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## Temperature sensors TRH
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Diagnostic Data | 0x0CF3 | 3316 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Battery voltage
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PowerLogic HeatTag
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
HeatTag Sensor | 0x0CF9 | 3322 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | HeatTag alarm type • 0 = No alarm • 1–15 = Low level alarm • 16–93 = Medium level alarm • 94–190 (except 99) = High level alarm • 99 = Test alarm (for more information on Test modes, refer to DOCA0171EN PowerLogic HeatTag - User Guide)
HeatTag Sensor | 0x0CFA | 3323 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | HeatTag alarm level • 0 = No alarm • 1 = Low level alarm • 2 = Medium level alarm • 3 = High level alarm
Ambient Data | 0x0FA0 | 4001 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Temperature value
Ambient Data | 0x0FA2 | 4003 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable temperature).
Ambient Data | 0x0FA4 | 4005 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable temperature).
Ambient Data | 0x0FA6 | 4007 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Relative humidity value Example: 50% represented as 0.50
Ambient Data | 0x0FA8 | 4009 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Maximum value that the device is able to read (maximum measurable humidity).
Ambient Data | 0x0FAA | 4011 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Minimum value that the device is able to read (minimum measurable humidity).
Ambient Data | 0x0FAC | 4013 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Air quality index • 0 = Good without triggered alarm • 1–9 = Intermediate without triggered alarm • 10 = Bad with triggered alarm (register 3322 and 3323)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
HeatTag Sensor | 0x79C7 | 31176 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Operation mode • 0 = Test mode (0–30 minutes after HeatTag sensor is powered on • 1 = Auto-learning mode (30 minutes–8 hours after HeatTag sensor is powered on) • 2 = Normal operation mode (>8 hours after HeatTag sensor is powered on)

## Acti9 Active
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Current Metering Data | 0x0BB7 | 3000 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase A
Current Metering Data | 0x0BB9 | 3002 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase B
Current Metering Data | 0x0BBB | 3004 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS current on phase C
Voltage Metering Data | 0x0BD3 | 3028 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage A-N
Voltage Metering Data | 0x0BD5 | 3030 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage B-N
Voltage Metering Data | 0x0BD7 | 3032 | 2 | R | - | V | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RMS phase-to-neutral voltage C-N
Power Metering Data | 0x0BED | 3054 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase A
Power Metering Data | 0x0BEF | 3056 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase B
Power Metering Data | 0x0BF1 | 3058 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Active power on phase C
Power Metering Data | 0x0BF3 | 3060 | 2 | R | - | W | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total active power
Power Metering Data | 0x0BFB | 3068 | 2 | R | - | VAR | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total reactive power
Power Metering Data | 0x0C03 | 3076 | 2 | R | - | VA | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total apparent power (arithmetic)
Power Factor Metering Data | 0x0C0B | 3084 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Total power factor
Power Factor Metering Data | 0x0C0D | 3086 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power factor sign convention • 0 = IEC • 1 = IEEE
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Energy Data - Legacy Zone | 0x0C83 | 3204 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Total active energy delivered + received (not resettable)
Energy Data - Legacy Zone | 0x0CB7 | 3256 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered + received (resettable)
Energy Data - Legacy Zone | 0x0CBB | 3260 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CBF | 3264 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CC3 | 3268 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CC7 | 3272 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial active energy received (resettable)
Energy Data - Legacy Zone | 0x0CCB | 3276 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial active energy received counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CCF | 3280 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy delivered (resettable)
Energy Data - Legacy Zone | 0x0CD3 | 3284 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy delivered counter. The value returns to zero by Panel Server.
Energy Data - Legacy Zone | 0x0CD7 | 3288 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Partial reactive energy received (resettable)
Energy Data - Legacy Zone | 0x0CDB | 3292 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | N | 3, 100-4, 16 | Set partial reactive energy received counter. The value returns to zero by Panel Server.
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE5 | 3302 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase B when voltage loss occurred
Load Monitoring - Alarm | 0x0CE7 | 3304 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase A when voltage loss occurred
Load Monitoring - Alarm | 0x0CE9 | 3306 | 2 | R | - | A | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Last RMS current measured on phase C when voltage loss occurred
Load Monitoring - Alarm | 0x0CF5 | 3318 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3319 • Bit 0 = Validity of Long-time protection alarm • Bit 1 = Validity of Short-time protection alarm • Bit 4 = Validity of Earth-leakage protection alarm • Bit 7 = Validity of AAF protection (Serial) alarm • Bit 8 = Validity of AAF protection (Parallel) alarm • Bit 12 = Validity of Push-button test alarm • Bit 13 = Validity of Internal cause alarm • Bit 14 = Validity of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0CF6 | 3319 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Long-time protection alarm • Bit 1 = Status of Short-time protection alarm • Bit 4 = Status of Earth-leakage protection alarm • Bit 7 = Status of AAF protection (Serial) alarm • Bit 8 = Status of AAF protection (Parallel) alarm • Bit 12 = Status of Push-buttton test alarm • Bit 13 = Status of Internal cause alarm • Bit 14 = Status of Tripping chain failure alarm
Load Monitoring - Alarm | 0x0CF7 | 3320 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the pre-alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3321 • Bit 0 = Validity of Overload ratio from trip threshold alarm • Bit 1 = Validity of Overvoltage ratio from trip threshold alarm • Bit 2 = Validity of Earth-Leakage ratio from trip threshold alarm
Load Monitoring - Alarm | 0x0CF8 | 3321 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Pre-alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Overload ratio from trip threshold alarm • Bit 1 = Status of Overvoltage ratio from trip threshold alarm • Bit 2 = Status of Earth-Leakage ratio from trip threshold alarm
Protection Against Ground Faults | 0x0D25 | 3366 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Ground fault level
Protection Against Ground Faults | 0x0D27 | 3368 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Pre-alarm on overload tripping threshold
Protection Against Ground Faults | 0x0D29 | 3370 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Pre-alarm on overvoltage tripping threshold
Protection Against Ground Faults | 0x0D2B | 3372 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Pre-alarm on earthleakage current tripping threshold
Energy Data – New Zone | 0x1390 | 5009 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy delivered (resettable)
Energy Data – New Zone | 0x1394 | 5013 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1398 | 5017 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy received (resettable)
Energy Data – New Zone | 0x139C | 5021 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy received count negatively (not resettable)
Energy Data – New Zone | 0x13B8 | 5049 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A delivered (resettable)
Energy Data – New Zone | 0x13BC | 5053 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x13C0 | 5057 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase A received (resettable)
Energy Data – New Zone | 0x13C4 | 5061 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase A received (not resettable)
Energy Data – New Zone | 0x13E0 | 5089 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B delivered (resettable)
Energy Data – New Zone | 0x13E4 | 5093 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x13E8 | 5097 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase B received (resettable)
Energy Data – New Zone | 0x13EC | 5101 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase B received (not resettable)
Energy Data – New Zone | 0x1408 | 5129 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C delivered (resettable)
Energy Data – New Zone | 0x140C | 5133 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x1410 | 5137 | 4 | RW | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Active energy on phase C received (resettable)
Energy Data – New Zone | 0x1414 | 5141 | 4 | R | - | Wh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Active energy on phase C received (not resettable)
Energy Data – New Zone | 0x1438 | 5177 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy delivered (resettable)
Energy Data – New Zone | 0x143C | 5181 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy delivered count positively (not resettable)
Energy Data – New Zone | 0x1448 | 5193 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy received (resettable)
Energy Data – New Zone | 0x144C | 5197 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy received count negatively (not resettable)
Energy Data – New Zone | 0x1470 | 5233 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A delivered (resettable)
Energy Data – New Zone | 0x1474 | 5237 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A delivered (not resettable)
Energy Data – New Zone | 0x1478 | 5241 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase A received (resettable)
Energy Data – New Zone | 0x147C | 5245 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase A received (not resettable)
Energy Data – New Zone | 0x1498 | 5273 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B delivered (resettable)
Energy Data – New Zone | 0x149C | 5277 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B delivered (not resettable)
Energy Data – New Zone | 0x14A0 | 5281 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase B received (resettable)
Energy Data – New Zone | 0x14A4 | 5285 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase B received (not resettable)
Energy Data – New Zone | 0x14C0 | 5313 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C delivered (resettable)
Energy Data – New Zone | 0x14C4 | 5317 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C delivered (not resettable)
Energy Data – New Zone | 0x14C8 | 5321 | 4 | RW | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Reactive energy on phase C received (resettable)
Energy Data – New Zone | 0x14CC | 5325 | 4 | R | - | VARh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Reactive energy on phase C received (not resettable)
Energy Data – New Zone | 0x14F4 | 5365 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy delivered + received (resettable)
Energy Data – New Zone | 0x14F8 | 5369 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy delivered + received (not resettable)
Energy Data – New Zone | 0x150C | 5389 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase A (resettable)
Energy Data – New Zone | 0x1510 | 5393 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase A (not resettable)
Energy Data – New Zone | 0x1534 | 5429 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase B (resettable)
Energy Data – New Zone | 0x1538 | 5433 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase B (not resettable)
Energy Data – New Zone | 0x155C | 5469 | 4 | RW | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4, 16 | Apparent energy on phase C (resettable)
Energy Data – New Zone | 0x1560 | 5473 | 4 | R | - | VAh | INT64 |  | 0x8000000000000000 | Y | 3, 100-4 | Apparent energy on phase C (not resettable)
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Configuration | 0x7926 | 31015 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Phase sequence with: • 1 = Phase A • 2 = Phase B • 3 = Phase C • 4 = Phase sequence ABC or AB • 5 = Phase sequence ACB or AC • 6 = Phase sequence BCA or BC • 7 = Phase sequence BAC or BA • 8 = Phase sequence CAB or CA • 9 = Phase sequence CBA or CB
Configuration | 0x7929 | 31018 | 1 | R | - | A | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Rated current of the protective device to the wireless device
Configuration | 0x792B | 31020 | 2 | R | - | V | Float32 |  | 0xFFC00000 | Y | 3, 100-4 | Rated voltage: • LN rated voltage for single phase wiring systems • LL rated voltage for 3 phases wiring systems
Configuration | 0x792D | 31022 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the commodity of the wireless device 1. Electricity 2. Gas 3. Fuel oil 4. Air 5. Steam 6. Water 7. Environment 8. Other 9. Custom (Free text to enter): User can enter 10 custom values
Configuration | 0x792F | 31024 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Power supply type • 1 = Top • 2 = Bottom (default value)
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Circuit breaker | 0x80E8 | 33001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker position • 0 = Open • 1 = Close

## Wireless indication auxiliary
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Device Temperature Metering Data | 0x0C3B | 3132 | 2 | R | - | °C | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Device internal temperature
Load Monitoring - Alarm | 0x0CE1 | 3298 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Validity of the alarm bitmap (0 = Invalid / 1 = Valid) – refer to register 3300 • Bit 0 = Validity of Voltage phase loss alarm(1) • Bit 1 = Validity of Current overload when voltage loss alarm(1) • Bit 2 = Validity of Current short-circuit alarm • Bit 3 = Validity of Current alarm 45% alarm(1) • Bit 4 = Validity of Load current loss alarm(1) • Bit 5 = Validity of Overvoltage 120% alarm(1) • Bit 6 = Validity of Undervoltage 80% alarm(1) • Bit 7 = Validity of Battery low pre-alarm(2) • Bit 8 = Validity of Heat alarm status alarm(3) • Bit 9 = Validity of Battery low alarm(4) • Bit 10 = Validity of Preventive maintenance on the device alarm(5) • Bit 11 = Validity of Device Replacement alarm(6) • Bit 12 = Validity of Current Alarm 50%(1) • Bit 13 = Validity of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Load Monitoring - Alarm | 0x0CE3 | 3300 | 2 | R | - | - | BITMAP |  | 0x00000000 | N | 3, 100-4 | Alarm bitmap status (0 = Inactive / 1 = Active) • Bit 0 = Status of Voltage phase loss alarm(1) • Bit 1 = Status of Current overload when voltage loss alarm(1) • Bit 2 = Status of Current short-circuit alarm • Bit 3 = Status of Current alarm 45% alarm(1) • Bit 4 = Status of Load current loss alarm(1) • Bit 5 = Status of Overvoltage 120% alarm(1) • Bit 6 = Status of Undervoltage 80% alarm(1) • Bit 7 = Status of Battery low pre-alarm(2) • Bit 8 = Status of Heat alarm status alarm(3) • Bit 9 = Status of Battery low alarm(4) • Bit 10 = Status of Preventive maintenance on the device alarm(5) • Bit 11 = Status of Device Replacement alarm(6) • Bit 12 = Status of Current Alarm 50%(1) • Bit 13 = Status of Current Alarm 80%(1) • Bit 14–31 = Reserved (1) Applicable on product families in tabs PTE63-PoTag QO, PTEnergy250_630-PoTag Efram, PTE Rope-PoTag Rope, Acti9 Active (2) Applicable on product families in tabs Wireless indication auxiliary, CL110, CO2 sensors, Temperature sensors TRH (3) Applicable on product family in tab HeatTag (4) Applicable on product family in tab Wireless indication auxiliary (5) Applicable on product families in tabs HeatTag (Fan Error), Acti9 Active (RCD Trip reminder) (6) Applicable on product family in tab HeatTag
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Configuration | 0x7925 | 31014 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Circuit breaker | 0x80E8 | 33001 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker position • 0 = Open • 1 = Close
Circuit breaker | 0x80E9 | 33002 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip indicator • 0 = Off • 1 = On
Circuit breaker | 0x80EA | 33003 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Circuit breaker trip electrical fault indicator • 0 = Off • 1 = On
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84E7 | 34024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 1 circuit identifier
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84EC | 34029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84F8 | 34041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Logical status of the Digital Input 1 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value

## Partial Discharge Box
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server

## PowerTagC2DI
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84D0 | 34001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Digital Input 1 name
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84E7 | 34024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 1 circuit identifier
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84EA | 34027 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84EC | 34029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84ED | 34030 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input 1 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84F8 | 34041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x84FE | 34047 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position - Only available if input assigned to OF (case = 2) ENUM { Open= 0, Closed = 1 Undetermined = 65535 // Invalid value } CircuitPositionID
Digital input | 0x8508 | 34057 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip ENUM { ON = 0, // Tripped OFF = 1 // Not tripped Undetermined = 65535 // Invalid value } Status
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Logical status of the Digital Input 1 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Digital input | 0x8534 | 34101 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Digital Input 2 name
Digital input | 0x854B | 34124 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 2 circuit identifier
Digital input | 0x854E | 34127 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Digital input | 0x8550 | 34129 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Digital input | 0x8551 | 34130 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input 2 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Digital input | 0x855C | 34141 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 2 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x8562 | 34147 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position - Only available if input assigned to OF (case = 2) ENUM { Open= 0, Closed = 1 Undetermined = 65535 // Invalid value } CircuitPositionID
Digital input | 0x856C | 34157 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip ENUM { ON = 0, // Tripped OFF = 1 // Not tripped Undetermined = 65535 // Invalid value } Status
Digital input | 0x8574 | 34165 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Logical status of the Digital Input 2 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Digital input | 0x8598 | 34201 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 1 when Digital Input 1 is defined as 'Custom'
Digital input | 0x85A2 | 34211 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital input | 0x85AC | 34221 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital input | 0x8660 | 34401 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 2 when Digital Input 2 is defined as 'Custom'
Digital input | 0x866A | 34411 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 2 when the Digital Input 2 is defined as 'Custom'
Digital input | 0x8674 | 34421 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 2 when the Digital Input 2 is defined as 'Custom'

## PowerTagCIO
Section | Address (hexa) | Register (dec) | N° | RW | X | Unit | Type | Range | Invalid Value | Saved | Function Code | Description
Identification | 0x7724 | 30501 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Product ID of the Panel Server
Identification | 0x7725 | 30502 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | Y | 3, 100-4 | Commercial reference of the Panel Server
Identification | 0x7735 | 30518 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | Y | 3, 100-4 | Firmware version of the Panel Server Example - xxx.yyy.zzz
Identification | 0x773B | 30524 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Serial number of the Panel Server
Identification | 0x7745 | 30534 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | Y | 3, 100-4 | Product model of the Panel Server
Configuration | 0x7918 | 31001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Device name of the wireless device. The user can enter maximum 20 characters.
Configuration | 0x7922 | 31011 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Label of the wireless device. The user can enter maximum five characters.
Device Identification | 0x7931 | 31026 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Virtual Modbus server address
Device Identification | 0x7932 | 31027 | 4 | R | - | - | UINT64 |  | 0xFFFFFFFFFFFFFFFF | Y | 3, 100-4 | Wireless device radio frequency identifier (RF-Id)
Device Identification | 0x7937 | 31032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Wireless product identifier
Device Identification | 0x7944 | 31045 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Vendor name
Device Identification | 0x7954 | 31061 | 16 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000000000000000000000000000 | N | 3, 100-4 | Commercial reference
Device Identification | 0x7964 | 31077 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Firmware revision
Device Identification | 0x796A | 31083 | 6 | R | - | - | ASCII |  | 0x000000000000000000000000 | N | 3, 100-4 | Hardware revision
Device Identification | 0x7970 | 31089 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | N | 3, 100-4 | Serial number
Device Identification | 0x797A | 31099 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product range
Device Identification | 0x7982 | 31107 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product model
Device Identification | 0x798A | 31115 | 8 | R | - | - | ASCII |  | 0x00000000000000000000000000000000 | N | 3, 100-4 | Product family
Diagnostic Data | 0x79A8 | 31145 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Validity of the RF communication between PowerTag system and Panel Server status. • 0 = Invalid • 1 = Valid
Diagnostic Data | 0x79A9 | 31146 | 1 | R | - | - | BITMAP |  | 0x0000 | N | 3, 100-4 | Communication status between Panel Server and wireless devices. • 0 = Communication loss • 1 = Communication OK
Diagnostic Data | 0x79AA | 31147 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Packet Error Rate (PER) of the device, received by Panel Server
Diagnostic Data | 0x79AC | 31149 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI of the device, received by Panel Server
Diagnostic Data | 0x79AE | 31151 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Link Quality Indicator (LQI) of the device, received by Panel Server
Diagnostic Data | 0x79AF | 31152 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER of gateway, calculated inside the Panel Server
Diagnostic Data | 0x79B1 | 31154 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | Radio Signal Strength Indicator (RSSI) calculated inside the Panel Server
Diagnostic Data | 0x79B3 | 31156 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI, calculated inside the Panel Server
Diagnostic Data | 0x79B4 | 31157 | 2 | R | - | - | Float32 |  | 0xFFC00000 | N | 3, 100-4 | PER – Maximum value between device and Panel Server
Diagnostic Data | 0x79B6 | 31159 | 2 | R | - | dBm | Float32 |  | 0xFFC00000 | N | 3, 100-4 | RSSI – Minimal value between device and Panel Server
Diagnostic Data | 0x79B8 | 31161 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | LQI – Minimal value between device and Panel Server
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84D0 | 34001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Digital Input 1 name
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84E7 | 34024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Digital Input 1 circuit identifier
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84EA | 34027 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84EC | 34029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to digital input 0 None 1 Custom 2 Circuit breaker status 3 Trip fault (SD) 4 Trip indicator synthesis 5 Trip elec fault (SDE) 6 Trip thermal fault (SDT) 7 Earth leakage fault 8 Ground fault 9 Surge arrester fault 10 Insulation fault 11 Circuit Breaker connected position 12 Circuit Breaker disconnected position 13 Circuit Breaker test position 14 Energy Reduction Maintenance Setting status 15 Door status 17 Drawer connected position 18 Drawer disconnected position 19 Drawer test position 20 Voltage loss 21 Advanced protection 22 Switch position 23 Fuse blown 24 Relay status 25 Trip circuit supervision 26 Emergency stop 27 Watchdog status 28 Source change over - A (Alternate) status 29 Source change over - Off status 30 Source change over - N (Normal) status 31 Motor preheating 32 Motor run 33 Motor start 34 Forced freewheel stop 35 Battery status 36 Battery end of autonomy 37 UPS status 38 UPS running mode 39 Auxiliary supply status 40 Tariff 1 Status 41 Tariff 2 Status 42 Tariff 3 Status 43 Tariff 4 Status 44 Tariff 5 Status 45 Flood detection 46 Under temperature 47 Over temperature 48 Process mode 49 Equipment status 50 Fan status 51 Standard Input Low-High 52 Standard Input 0V-24V 53 Standard Input Disconnected-Off 54 Standard input
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84ED | 34030 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Polarity of the Digital Input 1 Meaning of input: /0 for inactive/1 for active/: // Input Electrical status = 0V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) // // Input Electrical status = 230V or 24V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // or Meaning of input: /1 for inactive/0 for active/ // Input Electrical status = 0V --> input is active (eg: Trip fault (SD) = ‘Fault’ / Motor run = ‘Run’) // // Input Electrical status = 230V or 24 V --> input is inactive (eg: Trip fault (SD) = ‘No Fault’ / Motor run = ‘Off’) //
Modbus Registers of Wireless Indication Auxiliaries for ComPacT NSX and ComPacT NSXm Circuit Breakers | 0x84F8 | 34041 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Digital Input 1 electrical status. Indicates the electrical status of the input, regardless of the assignment reference & polarity • 0 = Low level • 1 = High level
Digital input | 0x84FE | 34047 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the breaker position - Only available if input assigned to OF (case = 2) ENUM { Open= 0, Closed = 1 Undetermined = 65535 // Invalid value } CircuitPositionID
Digital input | 0x8508 | 34057 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Indicates the status of the trip ENUM { ON = 0, // Tripped OFF = 1 // Not tripped Undetermined = 65535 // Invalid value } Status
Digital input | 0x8510 | 34065 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Logical status of the Digital Input 1 (takes into account the configured polarity) ON // Active OFF // Inactive Undetermined // Invalid value
Digital input | 0x8598 | 34201 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 1 when Digital Input 1 is defined as 'Custom'
Digital input | 0x85A2 | 34211 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital input | 0x85AC | 34221 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 1 when the Digital Input 1 is defined as 'Custom'
Digital output | 0x9088 | 37001 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Name given by the user to the Digital Output. Can be used for the name of the asset controled by the DO, or to specify the user define connected product and/or the user defined output assignment. Maximum 20 Characters Name should be wriiten from MSB to LSB
Digital output | 0x909F | 37024 | 3 | R | - | - | ASCII |  | 0x000000000000 | Y | 3, 100-4 | Name of the circuit on witch the Output is wired. Max 5 Char. May be left empty if not applicable. The LSB of the last register will contain the 5th characters
Digital output | 0x90A2 | 37027 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Indicates the usage of the wireless device with: • 1 = Main/Incomer • 2 = Sub/Head of group • 3 = Heating • 4 = Cooling • 5 = HVAC • 6 = Ventilation • 7 = Lighting • 8 = Office Equipment • 9 = Cooking • 10 = Food refrigeration • 11 = Elevators • 12 = Computers • 13 = Renewable power source • 14 = Genset • 15 = Compressed air • 16 = Vapor • 17 = Machine • 18 = Process • 19 = Water system pumps • 20 = Other Sockets • 21 = Other • 22 = Electrical vehicle charging station • 23 = Loads associated with renewable power source • 24 = Plug loads • 25 = Air conditionning • 26 = Domestic hot water • 27 = Heating & air conditionning • 28 = Hot sanitary water • 29 = IT • 30 = Lighting (interior) • 31 = Lighting (exterior and park) • 32 = Mixed usages • 33 = Refrigeration • 34 = Special loads • 35 = Total • 36 = Transportation system • 37 = Water
Digital output | 0x90A4 | 37029 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | ENUM { Normal = 0, // Contactor Latched = 1, // Impulse Relay (Other values reserved) } OutputBehavior
Digital output | 0x90A7 | 37032 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | ENUM { Normally Open = 0, Normally Closed = 1, } DIContactTypeID
Digital output | 0x90A9 | 37034 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | ENUM { Disable = 0, Enable = 1 }
Digital output | 0x90AC | 37037 | 1 | R | - | - | UINT16 |  | 0xFFFF | Y | 3, 100-4 | Features assigned to output: 0 None 1 Custom 2 Circuit breaker status 22 Switch position 32 Motor run 54 StandardOutput
Digital output | 0x90BA | 37051 | 1 | RW | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4, 16 | ENUM { No command = 0 OffCommand = 1, // Switch to logical state Off. Accepted only if Output is configured as Normal mode (contactor). See Output behavior OnCommand = 2, // Switch to logical state On. Accepted only if Output is configured as Normal mode (contactor). See Output behavior ToggleCommand=3, // Toggle command is the only way to control the output when it is configured in latched mode (impulse relay) . See Output behavior. Toggle can be used for Normal mode too }
Digital output | 0x90BB | 37052 | 1 | R | - | - | UINT16 |  | 0xFFFF | N | 3, 100-4 | Reflect the last command sent to the output - Only significant if Output is configured to Contactor (see Output behavior). Otherwise is set to invalid value ENUM { OFF = 0 ON = 1, Undetermined = 65535 // Invalid value }
Digital output | 0x90EC | 37101 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text giving the context of use of the Digital Input 1 when Digital Output 1 is defined as 'Custom'
Digital output | 0x90F6 | 37111 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the inactive value of the Digital Input 1 when the Digital Output 1 is defined as 'Custom'
Digital output | 0x9100 | 37121 | 10 | R | - | - | ASCII |  | 0x0000000000000000000000000000000000000000 | Y | 3, 100-4 | Text defining the active value of the Digital Input 1 when the Digital Output 1 is defined as 'Custom'